FORM eSpec 61d2P-sa Revised 04/05 	COPYRIGHT © 2005 SHIPPENSBURG PUMP COMPANY, INC.
Shipco® IS A REGISTERED TRADEMARK OF SHIPPENSBURG PUMP CO., INC. 	PRINTED IN THE U.S.A. • BEIDEL PRINTING HOUSE, INC., 717-532-5063
SHIPPENSBURG PUMP COMPANY, INC., P.O. BOX 279, SHIPPENSBURG, PA 17257
PHONE 717-532-7321 • FAX 717-532-7704 • www.shipcopumps.com
_______________________________________________________________________________________
SUGGESTED CONTROL SPECIFICATIONS	SHIPCO® PUMPS
surge tank with 2 pumps
(To be added to Surge Unit Specification)

The unit manufacturer shall furnish, mount on the pump unit, and wire a NEMA 2 control cabinet with piano hinged door, enclosing the following:
2	Combination magnetic starters (having 3 overload relays) with circuit breakers and cover interlocks.
2	“On-Off-Standby Continuous” selector switches.
2	Pump running pilot lights.
1	Control Circuit disconnect switch with cover interlock.
1	Numbered terminal block.
1	Fused control circuit transformer when the motor voltage exceeds 130 volts.
2	Momentary contact “test” push buttons.
Control cabinet shall contain U.L. listed or recognized components. Control cabinet shall be listed and labeled by Underwriter’s Laboratory.
Control components shall be provided by the unit manufacturer for operation as follows: the pumps shall run continuously based on the manual selection of pump. The standby pump shall be activated by a level switch of the deaerator unit which when level drops in deaerator switch will turn on standby pump.
The installing contractor, in addition to the pump control(s), shall provide and install all low water burner cut-off switches, all low water alarms and all associated circuits in accordance with all local codes. 
The unit shall be factory tested as a complete unit and a certified test report of pump characteristics produced, which shall be submitted prior to shipment. The unit manufacturer shall furnish complete elementary and connection wiring diagrams, piping diagrams, and installation and operation instructions.
Manufacturer shall be Shippensburg Pump Company, Inc., Shippensburg, PA