FORM Spec CSC-B-D, Revised 07/11	COPYRIGHT © 2011 SHIPPENSBURG PUMP COMPANY, INC. 
Shipco® IS A REGISTERED TRADEMARK OF SHIPPENSBURG PUMP CO., INC. 	PRINTED IN THE U.S.A. • BEIDEL PRINTING HOUSE, INC., 717-532-5063
SHIPPENSBURG PUMP COMPANY, INC., P.O. BOX 279, SHIPPENSBURG, PA 17257
PHONE 717-532-7321 • FAX 717-532-7704 • www.shipcopumps.com
_______________________________________________________________________________________
SUGGESTED SPECIFICATIONS	SHIPCO® PUMPS
TYPE CSC-B-D CONDENSATE UNITS WITH Duplex MODEL D PUMPS
CAPACITY SCHEDULE MUST BE COMPLETED.
Furnish and install according to drawings and manufacturer’s instructions the quantity of CSC-B-D duplex condensation pump(s) as shown on the drawings. Each unit shall consist of (1) cylindrical welded steel receiver minimum 3/16" thick, (2) water pumps, (1) mechanical alternator, electrical controls and accessories.
The condensate receiver shall be of welded steel construction minimum 3/16" thick, horizontal with flat heads, supported on saddles and have a capacity as shown on the drawings. Receiver material and thickness shall be as shown on the drawings. The condensate receiver shall be equipped with the following: (1) inlet strainer, (1) externally adjustable 2-pole mechanical alternator, top and bottom shut-off water level gauge with automatic shut-off if glass is broken, (1) magnesium anode, dial thermometer, (2) pressure gauges for pump discharge, (2) bronze isolation valves between pump and receiver plus a valve in each bleed line installed for maintenance, and (2) lifting eyes. The receiver size shall be as shown on the drawings.
A cast iron basket inlet strainer with vertical self-cleaning bronze screen shall be provided for the receiver inlet.
The centrifugal water pumps shall be flange mounted on the receiver suction piping. The pump shall be close coupled vertical design, and shall have a cast bronze impeller that is bronze fitted to the cast iron pump housing with a renewable bronze wearing ring. The mechanical seal shall be rated for 250°F service. The entire pump assembly shall be permanently aligned and dynamically balanced to deliver its full rated capacity. The pump shall be driven by an industry standard motor “off the shelf.” The motor shall have a NEMA standard shaft. The horsepower and electrical characteristics shall be as shown on the drawings.
The pump manufacturer shall furnish, mount on the pump unit, and wire a U.L. labeled NEMA _____ control cabinet with hinged door, containing:
2	Combination magnetic starters (each having 3 overload relays) with circuit breakers and cover interlock for lock-out tag-out capability
2	“Automatic-Off” selector switches
2	Momentary contact “Test” push buttons
2	Pilot run lights
1	Numbered terminal strip
1	Removable control mounting plate
Each pump control circuit shall be completely independent of the other. The NEMA _____ mechanical alternator shall (1) change the operating sequence automatically after each cycle, (2) provide simultaneous operation under peak load conditions, and (3) operate the second pump automatically, should the active pump or its control fail. (Tank over 48” in diameter must use two float switches to control the pumps with an  electrical alternator in lieu of a mechanical alternator).

The unit shall have a float switch assembly NEMA _____ to turn on a high water alarm mounted in control panel with bell, light and silencing relay with dry contacts to access building management system alarm.
A control circuit transformer for each circuit shall be provided when the motor voltage is three phase or code requires 115 volt controls. All factory installed wiring shall be numbered for easy identification and the numbers shall coincide with those shown on the wiring diagrams.
The unit shall have a single point power connection.
The entire pump package will be U.L. labeled when a control panel is furnished.
The manufacturer shall furnish a certified pump performance test. The pump manufacturer shall furnish complete elementary and connection wiring diagrams, piping diagrams, and installation and operation instructions.
Manufacturer shall be Shipco® PUMPS, P.O. Box 279, Shippensburg, PA 17257.
Capacity Schedule (Required to complete suggested specifications).
TYPE CSC-B-D CONDENSATE PUMPS SCHEDULE:
Quantity: __________ Catalog No. __________ CSC-B-D
Receiver: __________ gallons, __________ " dia. x __________ " long x __________ " thick steel
Duplex condensate pumps each rated __________ GPM @ __________ PSIG with __________ HP, __________ RPM, Motor Enclosure __________
Supply electrical power characteristics: __________ volts, __________ phase, 60 cycles
Control voltage: 115 volts, 1 phase, 60 cycles,