FORM Spec DC-S&ECC-S, Revised 01/11	COPYRIGHT © 2011 SHIPPENSBURG PUMP COMPANY, INC. 
Shipco® IS A REGISTERED TRADEMARK OF SHIPPENSBURG PUMP CO., INC. 	PRINTED IN THE U.S.A. • BEIDEL PRINTING HOUSE, INC., 717-532-5063
SHIPPENSBURG PUMP COMPANY, INC., P.O. BOX 279, SHIPPENSBURG, PA 17257
PHONE 717-532-7321 • FAX 717-532-7704 • www.shipcopumps.com
_______________________________________________________________________________________
SUGGESTED SPECIFICATIONS	SHIPCO® PUMPS
TYPE DC or ECC SINGLE CONDENSATION PUMPS
CAPACITY SCHEDULE MUST BE COMPLETED.
Furnish and install according to drawings and manufacturer’s instructions the quantity of DC or ECC SINGLE condensation pump(s) as shown on the drawings. Each unit shall consist of (1) cast iron receiver, (1) water pump, (1) float switch, electrical controls and accessories.
The condensate receiver shall be manufactured of close-grained cast iron with a 20 year warranty against corrosion failure. The receiver shall be equipped with: (1) externally adjustable 2-pole float switch, top and bottom shut-off water level gauge with automatic shut-off if glass is broken, dial thermometer, (1) pressure gauge for pump discharge, (1) bronze isolation valve between pump and receiver plus a valve in each bleed line installed for maintenance, (2) lifting eye bolts (on receivers 25 gallon and larger). The receiver size shall be as shown on the drawings.
A cast iron basket inlet strainer with vertical self-cleaning bronze screen shall be provided for the receiver inlet.
The centrifugal water pump shall be flange mounted on the receiver. The pump shall be close coupled vertical design, and shall have a cast bronze impeller that is bronze fitted to the cast iron pump housing with a renewable bronze wearing ring. The mechanical seal shall be rated for 250°F service. The entire pump assembly shall be permanently aligned and dynamically balanced to deliver its full rated capacity. The pump shall be driven by an industry standard motor available "off the shelf." The motor shall have a NEMA standard shaft. The horsepower and electrical characteristics shall be as shown on the drawings.
The pump manufacturer shall furnish, mount on the pump unit, and wire a U.L. labeled NEMA _____ control cabinet with hinged door, containing:
1	Combination magnetic starter (having 3 overload relays) with circuit breaker and cover interlock for lock-out tag-out capability
1	“Automatic-Off” selector switch
1	Momentary contact “Test” push button
1	Pilot run light
1	Numbered terminal strip
1	Removable control mounting plate
A control circuit transformer for each circuit shall be provided when the motor voltage is three phase or code requires 115 volt controls. All factory installed wiring shall be numbered for easy identification and the numbers shall coincide with those shown on the wiring diagrams.
The unit shall have a float switch assembly labeled NEMA _____ to turn the pump on and off based on the water level in the tank.
The unit shall have a float switch assembly labeled NEMA _____ to turn on a high water alarm mounted in control panel with bell, light and silencing relay with dry contacts to access the building management system alarm.
The manufacturer shall furnish a certified pump performance test. The pump manufacturer shall furnish complete elementary and connection wiring diagrams, piping diagrams, and installation and operation instructions.
The entire pump package will be U.L. labeled when a control panel is furnished.
Manufacturer shall be Shipco® PUMPS, P.O. Box 279, Shippensburg, PA 17257.
Capacity Schedule (Required to complete suggested specifications).
TYPE DC-S OR ECC-S CONDENSATE PUMPS SCHEDULE:
Catalog No. __________ DC-S or ECC-S
Capacity: __________ GPM @ __________ PSIG with
__________ HP, __________ RPM, Motor Enclosure __________
Receiver: _______ gallons
Current: _______ phase, 60 cycles, __________ volts