FORM Spec DSS-GNu	COPYRIGHT © 2014 SHIPPENSBURG PUMP COMPANY, INC. 
Shipco® IS A REGISTERED TRADEMARK OF SHIPPENSBURG PUMP CO., INC. 	PRINTED IN THE U.S.A. • BEIDEL PRINTING HOUSE, INC., 717-532-5063
SHIPPENSBURG PUMP COMPANY, INC., P.O. BOX 279, SHIPPENSBURG, PA 17257
PHONE 717-532-7321 • FAX 717-532-7704 • www.shipcopumps.com
_______________________________________________________________________________________
SUGGESTED SPECIFICATIONS	SHIPCO® PUMPS
TYPE DSS-GNu SINGLE CONDENSATION PUMPS
CAPACITY SCHEDULE MUST BE COMPLETED.
Furnish and install according to drawings and manufacturer’s instructions the quantity of DSS-GNU SINGLE condensation pump(s) as shown on the drawings. Each unit shall consist of (1) stainless steel receiver, (1) 316 stainless steel water pump, (1) stainless steel internal float switch, electrical controls and accessories.
The condensate receiver shall be made out of stainless steel for years of service. The receiver shall be equipped with: (1) externally adjustable 2-pole all stainless steel float switch, top and bottom shut-off stainless steel water level gauge with automatic shut-off if glass is broken, stainless steel dial thermometer, (1) stainless steel pressure gauge for pump discharge, and (2) stainless steel lifting eyes (on receivers 21 gallon and larger). The receiver size shall be as shown on the drawings.
The centrifugal water pump shall be top mounted on the receiver. The stainless steel pump shall be of the two stage design with the stainless steel axial flow first stage impeller coupled to the second stage stainless steel impeller, by a compression coupling and drive pin. All pump metal material shall be completely stainless steel. The mechanical seal shall be rated for 250°F service. The entire pump assembly shall be permanently aligned and dynamically balanced to deliver its full rate capacity. The horsepower and electrical characteristics shall be as shown on the drawings. The axial flow first stage stainless steel impeller shall be mounted in a stainless steel suction column with stainless steel bearing supports and water lubricated silicone bearings. The entire stainless steel suction column shall be threaded and be replaceable as a complete assembly. The drive shaft to the axial flow impeller shall be stainless steel. The second stage enclosed stainless steel impeller and stainless steel pump. The Mechanical shaft seals shall be rated for 250°F service. Each pump shall be close coupled motor. Pump capacity, motor HP and RPM, electrical characteristics, and receiver size shall be as shown on the drawings.
The pump manufacturer shall furnish, mount on the pump unit, and wire a U.L. labeled NEMA _____ control cabinet with hinged door, containing:
1	Combination magnetic starter (having 3 overload relays) with circuit breaker and cover interlock for lock-out tag-out capability
1	“Automatic-Off” selector switch
1	Momentary contact “Test” push button
1	Pilot run light
1	Numbered terminal strip
1	Removable control mounting plate
A control circuit transformer for each circuit shall be provided when the motor voltage is three phase or code requires 115 volt controls. All factory installed wiring shall be numbered for easy identification and the numbers shall coincide with those shown on the wiring diagrams.
The unit shall have a float switch assembly labeled NEMA _____ to turn the pump on and off based on the water level in the tank.
The unit shall have a float switch assembly NEMA _____ to turn on a high water alarm mounted in control panel with bell, light and silencing relay with dry contacts to access the building management system alarm.
The entire pump package will be U.L. labeled when a control panel is furnished.
The manufacturer shall furnish a certified pump performance test. The pump manufacturer shall furnish complete elementary and connection wiring diagrams, piping diagrams, and installation and operation instructions.
Manufacturer shall be Shipco® PUMPS, P.O. Box 279, Shippensburg, PA 17257.
Capacity Schedule (Required to complete suggested specifications).
TYPE DSS-GNU CONDENSATE PUMPS:
Catalog No. __________ DSS-GNU
Capacity: __________ GPM @ __________ PSIG with
__________ HP, __________ RPM , Motor Enclosure __________
Receiver: _______ gallons, stainless steel
Current: _______ phase, 60 cycles, __________ volts