FORM Spec DSSF, Revised 5/21	COPYRIGHT © 2014 SHIPPENSBURG PUMP COMPANY, INC. 
Shipco® IS A REGISTERED TRADEMARK OF SHIPPENSBURG PUMP CO., INC. 	PRINTED IN THE U.S.A. • BEIDEL PRINTING HOUSE, INC., 717-532-5063
SHIPPENSBURG PUMP COMPANY, INC., P.O. BOX 279, SHIPPENSBURG, PA 17257
PHONE 717-532-7321 • FAX 717-532-7704 • www.shipcopumps.com
_______________________________________________________________________________________
SUGGESTED SPECIFICATIONS	SHIPCO® PUMPS
TYPE DSsF SINGLE CONDENSATION PUMPS
CAPACITY SCHEDULE MUST BE COMPLETED.
Furnish and install according to drawings and manufacturer’s instructions the quantity of DSSF SINGLE condensation pump as shown on the drawings. Each unit shall consist of (1) 1/4” thick stainless steel unpainted receiver, (1) submerged water pump, (1)  Programmable Logic Control System (PLC), electrical controls and accessories.
The condensate receiver shall be made out of 1/4” thick stainless steel and be polished and unpainted with an elevation of 4” stainless steel angle iron legs for help in keeping the environment sanitary. The receiver shall be equipped with: (1) 4X stainless steel combination temperature and liquid level transmitter that controls the pump. It will display pump status, level and temperature on a local touchscreen located on panel door, and also send 4-20 mAmp signals remotely, (1) high water alarm point, top and bottom shut-off stainless steel water level gauge with automatic shut-off if glass is broken, stainless steel dial thermometer, (1) stainless steel pressure gauge for pump discharge, and (2) stainless steel lifting eyes. The receiver size shall be a shown on the drawings.
The stainless steel basket inlet strainer with vertical self-cleaning bronze screen shall be provided for the receiver inlet.
The centrifugal water pump shall be submerged within the tank with the stainless steel TEFC washdown duty motor exposed, as well as, the pump discharge which will extend through the top of the unit. The pump inside the tank shall be close coupled design, and shall have a cast bronze impeller that is bronze fitted to the cast iron pump housing with a renewable bronze wearing ring. The mechanical seal shall be rated for 250°F service. The entire pump assembly shall be permanently aligned and dynamically balanced to deliver its full rated capacity. The horsepower and electrical characteristics shall be as shown on the drawings.
The pump manufacturer shall furnish, mount on the pump unit, and wire a U.L. labeled NEMA 4X stainless steel control cabinet with hinged door, containing:
1	Combination magnetic starter (having 3 overload relays) with circuit breaker and cover interlock for lock-out tag-out capability
1	“Automatic-Off” selector switch
1	Momentary contact “Test” push button
1	Pilot run light
1	Display for PLC in Color for Modbus or BACnet (4”, 7” or 15” screen)
1	Numbered terminal strip
1	Removable control mounting plate
A control circuit transformer for each circuit shall be provided when the motor voltage is three phase or code requires 115 volt controls. All factory installed wiring shall be numbered for easy identification and the numbers shall coincide with those shown on the wiring diagrams.
The unit shall have a NEMA 4X Combination temperature and level transmitter system with a high water point with dry contacts in control panel so as to access the building management system alarm.
The entire pump package will be U.L. labeled.
The manufacturer shall furnish a certified pump performance test. The pump manufacturer shall furnish complete elementary and connection wiring diagrams, piping diagrams, and installation and operation instructions.
Manufacturer shall be Shipco® PUMPS, P.O. Box 279, Shippensburg, PA 17257.
Capacity Schedule (Required to complete suggested specifications).
TYPE DSSF CONDENSATE PUMPS:
Catalog No. __________ DSSF
Capacity: __________ GPM @ __________ PSIG with
__________ HP, __________ RPM , motor TEFC stainless steel washdown duty
Receiver: _______ gallons, polished and unpainted stainless steel 1/4” thick with 4” stainless steel legs
Current: _______ phase, 60 cycles, __________ volts