FORM Spec EMH, Revised 01/11	COPYRIGHT © 2011 SHIPPENSBURG PUMP COMPANY, INC. 
Shipco® IS A REGISTERED TRADEMARK OF SHIPPENSBURG PUMP CO., INC. 	PRINTED IN THE U.S.A. • BEIDEL PRINTING HOUSE, INC., 717-532-5063
SHIPPENSBURG PUMP COMPANY, INC., P.O. BOX 279, SHIPPENSBURG, PA 17257
PHONE 717-532-7321 • FAX 717-532-7704 • www.shipcopumps.com
_______________________________________________________________________________________
SUGGESTED SPECIFICATIONS	SHIPCO® PUMPS
TYPE EMH BOILER FEED UNITS
CAPACITY SCHEDULE MUST BE COMPLETED.
Furnish and install according to drawings and manufacturer’s instructions the quantity of EMH boiler feed units as shown on the drawings. Each unit shall consist of (1) steel receiver minimum 3/16" thick with a quantity of ______ boiler feed pumps, electrical controls and accessories.
The boiler feed receiver shall be of welded steel minimum 3/16", horizontal with flat heads and have a capacity as shown on the drawings. Receiver material and thickness shall be as shown on the drawings. The boiler feed receiver shall be equipped with the following: (1) top and bottom shut-off water level gauge with automatic shut-off if glass is broken, (1) dial thermometer, (1) mechanical make-up water assembly (max. city water 50 PSIG) and (1) magnesium anode. A bronze suction isolation valve between receiver and pump plus a valve in each bleed line installed for maintenance to permit servicing the pumps without draining the receiver.
A cast iron basket inlet strainer with horizontal self-cleaning bronze screen shall be provided for the receiver inlet.
The mechanical make-up water assembly shall be sized to equal the capacity of one of the boiler feed pumps (max. water 50 PSIG).
The boiler feed pumps shall be flange mounted on the receiver suction piping. The pump shall be close coupled vertical design, and shall have a cast bronze impeller that is bronze fitted to the cast iron pump housing with a renewable bronze wearing ring. The mechanical seal shall be rated for 250°F service. The entire pump assembly shall be permanently aligned and dynamically balanced to deliver its full rated capacity. The pump shall be driven by an industry standard motor available “off the shelf.” The motor shall have a NEMA standard shaft. The horsepower and electrical characteristics shall be as shown on the drawings.
The manufacturer shall furnish a certified pump performance test. The pump manufacturer shall furnish complete elementary and connection wiring diagrams, and installation and operation instructions.
Electrical control specifications must be added. See electrical specifications for boiler feed pumps.
The entire pump package will be U.L. labeled when a control panel is furnished.
Manufacturer shall be Shipco® PUMPS, P.O. Box 279, Shippensburg, PA 17257.
Capacity Schedule (Required to complete suggested specifications).
TYPE EMH BOILER FEED PUMPS SCHEDULE:
Receiver: __________ gallons, __________ " dia. x __________ " long x __________ " thick steel
Quantity: __________ boiler feed pumps each rated __________ GPM @ __________ PSIG
_________ HP, 3500 RPM , Motor Enclosure _________
Supply electrical power characteristics: __________ volts, __________ phase, 60 cycles
Control voltage: 115 volts, 1 phase, 60 cycles
Water supply pressure _________ PSIG,